Attachment “A”

January 9, 2014
Pennsylvania Department Of Transportation

Specifications For Maintenance And Operation

Of Greene County Welcome Center (Site “D”)

Wastewater Treatment System
I. GENERAL

A.
Purpose and Location
1. The Pennsylvania Department of Transportation, hereafter referred to as PENNDOT, requires the complete maintenance and operation of the wastewater treatment system consistent with standard operating procedures and applicable federal, state and local rules and regulations for the protection of the public health and the environment.

2. The facility is located along Interstate 79 northbound, at approximately mile marker #6 in Whitely Township, Greene County.   

B.
Renewal Option

1.
The contract will be for a period of one year from the effective date.  The contract will be renewed by mutual consent for two additional two-year periods.  Each Renewal, unit prices will be increased by four percent (4%)   
C. Scope of Work and Facility Description

As an integral part of this contract the awarded contractor and the assigned Wastewater Treatment Plant operator must review the Wastewater Treatment Plant Site and contract requirements with the District Roadside Specialist.  This meeting will be limited to two (2) hours and no payment will be made for this meeting.

1. Contract services will include performing all necessary operations, maintenance, trouble shooting, and repairs of the wastewater treatment facility, which include, but are not limited to supplying required chemicals, discharge and process control sampling, laboratory analyses, record keeping, report preparation and submission, equipment and preventive 

maintenance, and responsible, efficient and effective on-site management, supervision and staffing of the facilities. 

2. The wastewater treatment plant at Welcome Center Site “D” is a 9,500 GPD extended aeration sewage treatment plant having the following components:

· In-line flow equalization tank with transfer pumps

· Duplex aeration tanks and clarifiers

· Tertiary sand filter

· Waste activated sludge holding tank

· Ultraviolet disinfection

D. Contractor Qualifications 

1.
To receive consideration as a bidder for this contract, Contractor will provide written documentation of its capability to satisfactorily handle all aspects of the services’ covered under the scope of this contract.  The following documentation must be included with the Contractor’s bid:
· Copy of the lead or chief operator’s wastewater certification and certificate number. 

· Copy of the backup operator’s wastewater certification and certificate number. 

· Contractor’s Accredited Environmental Laboratory identification number and name as registered with the Department of Environmental Protection (DEP).
If you experience difficulty attaching your documents, please contact the Supplier Service Center at (877) 435-7363 and choose option #1.


E. 
Liability
1. The contractor will be responsible for taking all reasonable precautions, in accordance with sound industrial practices, to safeguard and protect from damage, all PENNDOT property and PENNDOT issued equipment.  The contractor will be responsible for the repair or replacement, in kind, of any lost or damaged property or issued equipment, excluding loss resulting from normal equipment wear in performing operation and maintenance duties.  

2.
The contractor shall report all acts of vandalism to the District Roadside Specialist or other designated PENNDOT representative and the Pennsylvania State Police within three (3) hours of the contractor’s knowledge of the occurrence

3.  An insurance certificate verifying coverage must be furnished to PENNDOT prior to issuance of the Notice to Proceed.  The provisions of the certificate cannot be canceled or changed until a 30-day prior written notice has been given to the Commonwealth.  Except as otherwise specified, the contractor is also responsible for damage claims as outlined in the PENNDOT specifications Publication 408 Section 107.14.

F.
Surety Provisions 

1. No bid security or performance bonding is required on this project.
G.  Bidding Reservation Clause 

      1.
PENNDOT reserves the right to reject any or all proposals and advertise for new proposals; if, in the judgment of the Secretary of Transportation, such actions will best serve the interests of the Commonwealth.

H.  Laws, Ordinances, and Fees 

1. The contractor will comply with all federal, state and local laws, ordinances, rules and regulations as applicable and as may be set forth by PENNDOT covering specified contract work.

2. The contractor shall acquire the necessary permits, licenses and certifications and assume all financial responsibility for acquisition.  PENNDOT will be responsible for renewing the National Pollutant Discharge Elimination System (NPDES) permit for the treatment plant. 

I. 
Basis for Payment

1. Payment for maintenance and operation will be made monthly at the unit price listed, this price shall include incidental operational equipment, materials, chemicals, supplies, Initial (within 30 days of start of contract) and follow-up Annual Flow-Meter Calibration and incidental routine wastewater sample collection and analyses as specified herein.

2. All labor and materials used for work performed must be documented on the “Daily Roadside Activity Report” (form M-609) supplied by PENNDOT.  The contractor’s representative and the PENNDOT District Roadside Specialist must sign this report.  This report will serve as basis for payment.   

3. The awarded purchase order will contain an item (s) for material contingency and on call repairs. Use of this item must be approved by the District Roadside Specialist before use.  All parts and materials will be paid at cost plus 15%.  All purchased items that exceed $20.00 must be supported by vendor invoice.    

4. Wastewater treatment plant waste sludge pumping, removal and disposal will be paid for based on the number of gallons of sludge pumped from the sludge holding tank and transported from the facility.  A record of the total quantity (gallons) removed must accompany all invoices for this service.
J. 
 Method of Payment
1.
At the end of each month, the contractor must submit an itemized invoice, to the bill to address as listed on the purchase order.  

K.  Safety Requirements

1. All work shall be conducted in a manner to insure the safety of the public and plant operators.  

2. The contractor shall provide all safety equipment necessary for the plant operators to perform the routine and specialized work in operating, repairing and maintaining the wastewater facilities.   Equipment shall include, but is not limited to, safety belts, aprons, goggles, disposable rubber gloves, disinfectant soap, locks and tags for control panels and other equipment and material as is appropriate for specific work tasks.

3. The contractor shall comply with all applicable Federal, State and local laws and safety regulations when entering confined spaces and shall not enter any tank, lift station wet well or enclosed treatment structure, or perform any activity that would be considered "Confined Space Entry" as defined by 29 CFR 1910.146 without appropriately trained personal and equipment.

4. All necessary equipment and provisions required for Confined Space Entry compliance shall be furnished by the contractor and will be incidental to the contract lump sum price.   
L.  
Noncompliance

1. If the contractor fails to comply with the requirements of the contract, Publication 408, Section 108.09 will prevail.  

2. Should the contractor fail to properly sample and perform any of the required tests designated herein, or fail to submit tests before the date stipulated, the contractor will be assessed liquidated damages in the amount of $500.00 per occurrence for each test or tests not properly performed or reported.  These assessments will be collected by reducing the dollar value of the invoices submitted or, if this amount is insufficient, by direct reimbursement to PENNDOT.  Split sample test results, which verify improper sampling, handling storage or testing will be resolved under the provisions of this section.

3. In the event the contractor fails to comply with any of the contract specifications or requirements through neglect of, or “planned” damages to, Department equipment or facilities to increase items of work, PENNDOT reserves the right upon 24-hour written notice to terminate the contract.  The defaulting contractor will be liable for all costs over and above the original contract incurred by the Department for the failure of the contractor to perform the work for the remainder of the contract period.

M.   Liquidated Damages

1.
The Department of Transportation reserves the right to assess liquidated damages in the amount of five hundred dollars ($500.00) per occurrence for any of the following circumstances.

· Failure to properly collect samples and perform any of the required tests.

· Failures to comply with any permit requirements.

· Damage to PENNDOT property and equipment through negligence.

· Failure to perform testing on specified schedule.

· Failure to immediately notify the District Roadside Specialist in the event of operational or mechanical failure.

· Incomplete discharge monitoring reports (DMRs) for two consecutive months.

· Failure of the contractor to maintain a 5-day schedule for operation of the facility.

· Split sample test results, which verify improper sampling, handling storage or testing.

· Failure of the operator to comply with sign in procedures of attendant’s master diary and punch provided time card. 
· Failure of contractor to provide all necessary routine maintenance, including but not limited to Building Cleaning, maintenance of sand filters, and general maintenance of wastewater building and surrounding grounds.
· Failure to comply with the DEP discharge permit limits for two or more consecutive months.  More than three months of non-compliance may result in termination of contract. 

· Failure of the contractor to develop the required “SOP” manual or provide the required maintenance schedule.

2.
On the second, and all subsequent occurrences where the contractor has failed to follow the testing and reporting procedures as outlined above, a $500.00 liquidated damage assessment will be made for each occurrence.

3.
Additional charges may be assessed as indicated in the specifications for respective items.  Multiple assessments of liquidated damages may be deemed contractor noncompliance and result in contract termination.

4.
The Welcome Center is open 24 hours per day.  The malfunction or shutdown of the wastewater treatment facility for any extended period of time will inherently result in closure of the Welcome Center facility, thereby adversely affecting services provided to the public.  It is mandatory that the contractor immediately responds to any on call occurrence and initiate uninterrupted repairs or replacements.  Proof that the most expeditious supply source for parts is being pursued will be required when work on system restoration is interrupted.  The Department may require a list of all contracted suppliers.  The contractor must provide sufficient in-house or subcontracted personnel, as approved by PENNDOT, to perform uninterrupted repairs or replacements.  Liquidated damages in the amount of $175.00 per hour following the second hour of interrupted service will be assessed for the failure to comply with the requirements of this paragraph.

N.   Mechanical Failure and System Repairs

1. The contractor shall prepare in writing a preventive maintenance program for maintaining and preserving the facility and system equipment. The contractor shall submit this plan to the Department for approval or revision and implement the approved plan upon the Departments approval. This plan shall be in effect and posted at the treatment plant within 45 days after contract effective date. The contractor will be liable for repairs resulting from lack of effective preventive maintenance.

     The contractor shall provide two additional copies of this plan to the Department within that time frame.  All revisions or addendums to this plan shall require the same number of copies provided to the Department.

2.
The Contractor shall be capable of responding to an on call request, 24 hours a day; 7 days a week.  Response should be within a reasonable period of time, but no later than two (2) hours following notification of the problem.  Failure of the contractor to respond within two (2) hours, under normal weather conditions, following a required call out by PENNDOT may result in termination of the contract in accordance with paragraph L (Non-Compliance) of these specifications.   

3. In the event any system failure or major mechanical breakdown occurs, the contractor is to evaluate the situation, determine the degree of repair required and immediately contact the District Roadside Specialist or the designated representative with a plan of corrective action.

4. When notifying the District Roadside Specialist of such required repairs, the contractor shall indicate the urgency of the repair and designate vendors who may accomplish such work in an expeditious, efficient and economical manner.

5.
Major repairs and mechanical replacements will require PENNDOT approval. Repairs shall be made only after a cost estimate is prepared and the District Roadside Specialist or designated representative verbally authorizes the work.  The contractor will notify the District Roadside Specialist of the date and time repairs will be performed.

6.
The contractor will be liable for all ensuing regulatory fines and sanctions and/or equipment repair costs should the outcome of contractor’s failure to properly notify the District Roadside Specialist of the needed repairs, or perform repairs in a timely manner, result in a violation of the operating permits or subsequent mechanical or electrical break down.     

7. PENNDOT retains the option to refuse any proposal for repairs and reserves the right to have repairs performed by PENNDOT personnel or by another contractor.

8. Unless otherwise directed, the contractor shall immediately remove all damaged parts and equipment from the site following a repair or replacement and retain the manufacturer’s warranties for all newly installed equipment at the site.


O.   Site Security
1.
The contractor shall properly secure the wastewater treatment facility within the limits of the existing security devices provided and insure that all gates, electrical control panels, buildings and grates are secure following each site visit.  
II.
OPERATION OF WASTEWATER TREATMENT FACILITIES
A.  Personnel

1. All employees of the contractor, operating and monitoring the wastewater treatment facilities, shall currently have a minimum Class D 1 sewage treatment plant operator certification in accordance with 25 Pa. Code § 302 (Certification of Operators) and as issued by the State Board for Certification of Sewage Treatment Plant and Waterworks Operators.   In addition, the contractor shall provide and designate a back-up operator, having the same certification, to be directly responsible for operation when the lead or chief operator is not available. 

2.   The contractor shall not allow unlicensed personnel to perform the duties of certified operators.  Only certified operators will make process control decisions.  All trainees shall be under the direct, on site supervision of an appropriate Class D 1 sewage treatment plant operator.  Violations of this provision will be sufficient grounds for termination of this contract.

3.
The contractor and all employee plant operators must be familiar with the conditions and requirements of the National Pollutant Discharge Elimination System (NPDES) permit governing the discharge of treated sewage at the Welcome Center’s wastewater treatment facility.  

· NPDES Permit No. PA0098434 (Exhibit I), PENNDOT Welcome Center Sewage Treatment Plant, Whiteley Township, Greene County.  

B.  Time of Operation

1. 
The operator shall be on duty a minimum of five (5) days per calendar week (Sunday through Saturday) for a minimum of one (1) hour on each such day during daylight hours, and for such additional time as necessary to perform all contractually required routine operational and maintenance tasks assigned under this contract, and as required in the NPDES discharge permit in order to produce a quality effluent and maintain permit compliance.

1. The operator will be "on call" during periods when the plant is unattended and must have a cell phone in the event the operator is needed on site. All call outs are an integral part of the monthly bid price and no additional payments are due to the contractor.
2. The pager and cell phone numbers must be given to the District Roadside Specialist and remain on file at the PENNDOT District Office throughout the term of the contract.

4.  The contractor, upon arrival at the Welcome Center will report to the Custodial Office, sign the site diary and punch the time card assigned to his contract.  After completing the assigned work the contractor will punch their time card out and initial in ink over the stamped time.  Time cards will be crosschecked with M-609 documentation and invoices.

       C.
Process Control and Performance Monitoring

1.  Only certified operators shall make process control decisions.  The lead certified operator shall develop STANDARD OPERATING PROCEDURES (SOP’s) specifically for the Welcome Center wastewater facility.  A copy of the standard operating procedures shall be retained on site in bound, typewritten form to direct the activities of non-certified operators. This “SOP” operational manual shall be completed within 45 days of the effective date of the contract. The contractor shall provide two additional copies of this manual to the Department within that time frame.  All revisions or addendums to this manual shall require the same number of copies provided to the Department.  Submission of electronic copies will be acceptable.
2. SOP’s shall include daily and monthly operational procedures and methodologies for process control, testing, record keeping and system adjustments, including chemical mixing and application rates.  The SOP’s must set operational limitations when non-certified operators take action to maintain system status.  

3. The certified operator shall determine the optimum range of operational and process controls necessary to achieve a high quality effluent and maintain permit compliance. During each site visit, the plant performance shall be monitored and evaluated and suitable operational adjustments implemented accordingly.

4. In addition to continuous flow measurement, performance monitoring and control testing of the treatment process shall include, but not be limited to, the following:

a. Dissolved Oxygen (DO) – Determine concentrations in the aeration tanks during each site visit.    

b. pH - Measure levels in the discharge and aeration tanks at each visit.

c. Mixed Liquor Suspended Solids (MLSS) - Measure levels in aeration tanks at least once each month.  

d.    
MLSS Settleability - During each visit, perform 30-minute settlometer test for each aeration tank.

e. Sludge Blanket Depth - Measure level in each clarifier during each site visit.

f. Alkalinity - Measure levels in aeration tanks at a frequency necessary to insure sufficient concentrations for the proper operational control and removal of ammonia nitrogen.

D.  Duties and Responsibilities
1. The contractor shall perform all maintenance and repairs in a manner that keeps the facilities and the associated equipment clean, serviceable and operating free of odors and health and safety hazards.

2. Routine maintenance shall include, but is not limited to, the following tasks:

· Troubleshooting and adjustment of equipment.

· Replacement of blower, air filters, belts and gear case oil.

· Cleaning air diffusers.

· Lubrication of pumps, motors and other wear points.

· Skimming and cleaning of scum baffles, weirs, troughs and weir boxes.

· Cleaning of tanks and other equipment including the bottom and sidewalls of the clarifier, chlorine contact and equalization tanks.

· Removal of floating material in the clarifier, chlorine contact tanks.

· Removal and proper disposal of accumulated screenings and trash. 

· Checking for proper operation of all air lifts and sludge return piping.

· Monitor and check all pump operation for clogging, bearing wear, seal leaks and motor heating.

· Decanting of the sludge holding tank.

· Furnishing and installing replacement flowmeter pens and recording charts as required. 
· Cleaning of Ultra violet disinfection unit:
·  Unit bulbs shall be cleaned monthly. , 
· Initial bulb replacement (within 30 days of start of contract) shall occur as an integral part of item 1 monthly cost.
· Follow-up bulb replacement shall occur annually as an integral part of item 1 monthly cost.

3.
Operation of the wastewater treatment plant will include maintaining the sewer line between the rest area building and the treatment plant and opening any blockages that may occur in the line.   

3. The contractor shall have an authorized manufacturer’s representative calibrate the flowmeter and certify the operation at least once each year and shall provide a written schedule of when these events will take place during the year.  The contractor shall submit documentation (copy of invoice) as to when these services were performed along with the name and certificate number of the certifier.  The flowmeter shall be labeled with the certification number and date of certification. Annual flowmeter calibration shall be an integral cost of the monthly operational price.

5. The contractor or plant operator will contact the District Roadside Specialist on a weekly basis to update the Department of treatment plant status.  This is incidental to the monthly plant operation bid price.

E.
Waste Treatment Restrictions 

1.
The treatment facility is solely for the purpose of treating wastewater from the Welcome Center facility.  Any septage or wastewater introduced from external sources will be cause for immediate cancellation of this contract.  The difference in cost between the canceled contract and the subsequent award will be assessed against the noncompliant contractor.  In addition, the noncompliant contractor will be liable for any fines, penalties, expenses or costs of any other nature resulting from the introduction of external wastewater into the plant or from the processes of contract cancellation and re-award.

F.
Equipment and Materials 

2. The contractor will furnish all necessary equipment and materials required for daily and preventative maintenance, plant operation, process control testing and sample collection.  The equipment and materials shall include but are not limited to, dissolved oxygen meter, pH meter, settleometer, colorimeter, composite sampler, flowmeter chart paper and pens, blower belts, hose, lubricants, tools and sampling and testing apparatus and reagents.

3. All costs associated with the purchase and delivery of chemical supplies to the wastewater treatment facility will be the contractor’s responsibility and incidental to the contract lump sum price.  The contractor is required to obtain, properly store, and effectively apply all essential chemicals in quantities as may be necessary for appropriate treatment plant operation in maintaining an effluent discharge within permit compliance.   Chemical supplies required for the various treatment processes will include, but are not necessarily limited to the following: 

· Alkalinity and pH adjustment  - Sodium bicarbonate, sodium carbonate (soda ash), magnesium hydroxide, sodium hydroxide (caustic soda), lime or other suitable chemical.

·  Bioaugmentation - Microorganisms and bacteria enzyme additives, such as nitrifying bacteria, as may be needed to enhance treatment efficiency of the biological systems. 

G.    Discharge Monitoring 

1.  The contractor is responsible for conducting all discharge monitoring in compliance with the facility’s NPDES discharge permit.  All expenses associated with sample collection and analysis shall be the sole responsibility of the contractor and incidental to the contract lump sum price.  In the event the Department requires a split sample, the contractor will provide all sterilized vessels necessary for sample collection.

2.   In accordance with the Environmental Laboratory Accreditation Act (Act 2002-25), all wastewater effluent sample collection and analysis, as required by the discharge permit, including pH and dissolved oxygen shall be performed by a DEP accredited laboratory.  Prior to April 2004, only DEP registered environmental laboratories will have interim authorization to collect and analyze effluent samples.  The contractor shall retain DEP authorization to collect and analyze effluent samples and maintain accreditation throughout the duration of the contract.

3.
The contractor will collect wastewater samples and arrange for laboratory test analysis of specific effluent discharge parameters, in accordance with the monitoring requirements summarized in Part A 1 of the discharge permit.  Approved laboratory procedures including holding times, sample collection and analytical methods, shall be in accordance with 40 CFR Part 136 (Code of Federal Regulations).

4.
All sampling points for monitoring plant performance shall be field located, marked and approval by the District Roadside Specialist.  Failure to use approved sampling points and/or sampling methods will require the contractor to resample and perform additional tests at no additional cost to PENNDOT.

5.    All monthly wastewater analyses for discharge parameters having a monitoring frequency of twice each month shall be completed within the first two (2) weeks of every month.  The contractor shall collect and analyze the first series of samples within the first seven (7) calendar days of each month, and schedule the remaining analyses, such that laboratory test results are received within adequate time to allow for any operational adjustments and additional sample testing, as may be required for discharge compliance prior to the end of the month.

6.    Upon receipt of all the monthly test results, the operator shall review each parameter’s discharge concentration for permit compliance.  Should any parameter’s average discharge concentration exceed the permit limit, determine the cause, immediately initiate corrective action and, after plant operation has stabilized, collect and analyze an additional sample for the noncompliant parameter(s).  The results of this analysis shall be incorporated with the previous values and a new monthly average concentration computed for permit compliance reevaluation.  Should the average concentration once again exceed the permit limit, implement remedial measures and repeat sampling/testing procedures as necessary to sustain permit compliance.

7.    Given that the treatment facility’s effluent quality is a reflection of the contractor’s operational performance, the contractor will be responsible for all costs incurred in collecting and analyzing supplementary samples.  Failure to adhere to the established discharge monitoring procedures will result in the assessment of liquidated damages. 

2. The results of all laboratory analyses shall be typed on the testing laboratory’s letterhead and forwarded to PENNDOT, along with each monthly discharge monitoring report.  In accordance with the NPDES permit requirements, the contractor and testing laboratory will be responsible for documenting the following information on each sample report form.

· Exact place, date, and time of sampling or measurement.     

· Name of the person who performed the sampling or measurement.

· Dates the analyses were performed.

·    Name of the person who performed the analyses.

· Analytical techniques or methods used.

· Results of analyses.

H.    Reporting, Record Keeping And Notification

3. Maintain complete records of all plant operations and maintenance and submit a monthly operating and discharge monitoring report (DMR) to PENNDOT and the Department of Environmental Protection (DEP).  A copy of the discharge permit must be on site at all times.

· An operations and maintenance log, designated as the daily operating logbook, shall be maintained for the wastewater facility and kept on site in a location accessible for twenty-four (24) hour inspection by PENNDOT representatives or the Department of Environmental Protection.  The log shall be current to the last operation and maintenance activity performed and shall include as a minimum the following entries and documentation:

· Treatment facility identification and discharge permit number.

· Name and certification number of lead operator.

· Signature of the attending operator following each daily entry.

· Date of visitation along with arrival and departure times.

· Specific maintenance activities performed.

· A clear and concise process control and operating summary of actions taken by the operator. 

· Results of all analytical process control and discharge monitoring testing.

· Amount of sludge wasted.

· Name of sludge hauler, amount of sludge pumped from the plant and disposal site.            

· Retain the flowmeter chart recordings in an orderly fashion along with the logbook.  

4.  Monthly monitoring results shall be summarized and reported on a copy of the Discharge Monitoring Report (DMR) form and Supplemental Sewage Sludge / Biosolids Production and Disposal Report included with the facility’s permit.  A supplemental monitoring report (Exhibits II) of daily records must be prepared and submitted along with the DMR to PENNDOT. All analytical test results must be submitted on laboratory letterhead and accompany the DMR submission.

3.  All discharge monitoring and supplementary reports, including copies of those sent to DEP will be submitted no later than the last day of each month to the following addresses:

PA Department of Transportation

      

Engineering District 12-0



      

825 North Gallatin Avenue



      

P.O. Box 459





            

Uniontown, PA 15401-0459







     




    Attn: Michael D Maurer, District Roadside Specialist

PA Department of Transportation

P. O. Box 3060

Harrisburg, PA  17105-3060

Attn:  Gary Yacisin

4.  Within 28 days following the end of the reporting period, the contractor      shall submit properly completed and signed discharge-monitoring reports to each the following:  

Department of Environmental Protection
                                     Attn:  Water Quality Specialist

Water Management  










    400 Waterfront Drive











    Pittsburgh, PA 15222-4745 




    Attn:  Water Quality Specialist

    Department of Environmental Protection




    California District Office





    

    25 Technology Drive







    California Technology Park




   Coal Center, PA 15423


5.    All DMR’s and supplementary reports shall be prepared and submitted in typewritten form, computer generated text document or spreadsheet format.  The contractor shall provide comments and fully explain any violation where indicated on the DMR form. Incorrect, incomplete or hand printed reports will be returned for revision and subsequent resubmission.  The contractor shall fully comply with the discharge permit non-compliance reporting procedures.

4. In the event that PENNDOT receives a notice of discharge violation from the Department of Environmental Protection (DEP), the plant operator will be required to prepare, or contribute to the preparation of, reply correspondence.  Should DEP request a field or office meeting as a result of discharge violations, the plant operator shall accompany the Department and be prepared to explain the cause of the violation and present the intended corrective actions for compliance.  Response preparation and/or meeting attendance will be incidental to the contract lump sum bid price.

 I.
Waste Disposal

1.
 Collected screenings, slurries and wet or dried sludge shall be handled and disposed of in compliance with the requirements of 25 Pa. Code, Article VIII, Municipal Waste and Article IX, Residual Waste Management as related to permits, forms and procedures necessary for the proper storage, landfilling, land application, incineration, and disposal of wet or dry sewage sludge.

2.
The contractor shall be responsible for pumping and disposal of waste activated sludge resulting from the treatment process, as well as insuring that contracted haulers have all necessary permits and approvals for the handling, storage, transport, and disposal of solid waste material generated as a result of wastewater treatment.  All waste sludge must be disposed at PA Department of Environmental Protection (DEP) approved sites in accordance with applicable DEP rules and regulations.  

3. The contractor must submit the sludge hauler’s invoice as well as the vendor’s disposal site, certification number and Form M-609 (Daily Roadside Activity Report). Invoices for sludge disposal services will be rejected unless accompanied by a manifest signed by the waste sludge hauler and the receiving wastewater treatment plant representative.  

13
Page 2 of 15

