PENNDOT 12-4 Electric Hot Water Pressure Washer system furnish and Install Specification

Scope:

PENNDOT Washington County is asking vendor to submit an all-inclusive price for furnishing and installing a total electric Hot Water pressure washer system in its Eighty-Four PA Maintenance Garage. This vendor will be responsible for all permitting, engineering, Electrical, Plumbing and machine installation. Vendor will be responsible for ensure system functionality and performance.

Location and delivery:

All work will need to be performed in the weld and wash bay’s in PENNDOT’s heavy truck maintenance garage located at 160 Route 519 in Eighty-Four PA 15330. All Travel time, and freight, expenses will be the awarded vendor’s responsibility. This Garage’s Normal Hours of operations are from 7am until 3pm M-F. The awarded vendor will have access to this facility between these hours to complete work as needed. In the event the awarded vendor must shut down Electrical power to the facility, this shutdown must be scheduled in advance for non-working hours with Washington Counties Maintenance Manager, Adam Smith, 724-223-4482, at least 5 business in advance of the power shut off.

Time Frame:

The awarded vendor will have 120 calendar days after they have received a notice to proceed and are emailed a fully executed purchase order for the project. After the 120 Day time frame the awarded vendor must hold a brief training session for 12-4’s Management staff and demonstrate the systems capabilities.

Mandatory Pre-Bid Conference:

There will be a mandatory pre-bid conference held at Washington Counties Maintenance garage on Tuesday January 9th @ 7:30am to go over the facilities Electrical and water access points. Vendors will need to sign an attendance sheet for this event. Only vendors that have attended this mandatory pre-bid conference will be eligible to bid on this Furnish and install contract. All other bids will be disqualified.

Permitting:

The awarded vendor will be responsible for gathering necessary permits from the Department of Labor and Industry for this installation. If no permits are required, the vendor must sign and provide an affidavit saying as such. Any engineering fees will be the responsibility of the awarded vendor. All permits and Engineered drawings will become the property of the Commonwealth at project completion.

Safety:

Awarded vendor will be responsible for complying with all PENNDOT, OSHA and PA DLI Safety Standards. Vendor will be responsible for Pedestrian safety near all work areas. Work areas are to be cordoned off by the contractor.

Electrical:

The awarded vendor will be responsible for Running and providing power to the pressure washer system as per their permit. PENNDOT has a breaker panel near the install location that the contractor may use to acquire necessary electrical power for the needs of their pressure washing system. PENNDOT has 120-volt power available for contractors use for tools and such during the install.  Vendor will be responsible for generating their own power during the event they need to shut down power to the facility for pressure washer installation.

Water supply:

Facility Water Lines are in the Wash Bay at the garage and the awarded vendor will be responsible for making necessary water connections to the pressure washing system.

Prevailing Wage:

Awarded vendor will be responsible for ensuring compliance to the Department of Labor and Industry’s Prevailing Wages act.

Equipment Specifications:

The below specifications are considered minimums for this project a vendor may be able to provide and install a system that meets or exceeds these specifications.  If a vendor provides a system that does not meet these minimum specifications they would the vendor will be in Default of the contract and will be responsible at their expense, to provide and install a unit that does meet the minimum requirements. The unit is to be of industrial capacity and be able to perform on an extreme duty schedule as it will be used to regularly wash all PENNDOT’s heavy equipment in that county and may be used 24 hours per day, 7 days per week. The awarded vendor shall be responsible for mounting an industrial style self-retracting hose reel in the was bay and a wand hanger. These two items must be of a corrosion resistant material and guaranteed by the awarded vendor for a minimum of three years.

Machine Specifications Below:

| Pressure | N/A 2500 psi |
| --- | --- |
| Pump Style | N/A Oil Bath Crankcase Positive Displacement Triplex |
| Motor Power | N/A 7 1/2 hp |
| Water Heater | N/A Replaceable 6 to 10000 W Stainless Steel Immersion Heater |
| Standard Parts/Features | N/A Temperature Control |
| Water Heater Power | N/A 6 to 10000 W |
| Current | N/A 75 A150 A |
| Heat Rise | N/A 85 ºF |
| Wand Type | N/A Trigger-Standard |
| Hose Diameter | N/A 3/8 in |
| Hose Length | N/A 100 ft |
| Flow Rate | N/A 3.5 gpm |
| Chemical Features | N/A Precise Metered |
| Float Tank Construction Material | N/A Stainless Steel Float Controlled |

Cleanup / Restoration:

The awarded vendor will be responsible for hauling away any construction / demolition debris created by this project. All department owned scrap metals will be disposed of properly in the scrap metal container on the departments property. The awarded vendor will be responsible for restoring the work areas to a like new condition prior to final inspection, this is to include painting, patching, dusting and cleaning as necessary.

Project Completion / Final Inspection:

The awarded vendor at the completion of the project, will be responsible for scheduling the final inspection for any permit requirements with the Department of Labor and Industry, the County Equipment Manager Jeff Huseman 724-223-4490, the District Facility Administrator Orin Summy 724-415-1050 and the Purchasing Agent 2 Chris Inman 724-439-7348.

Vendor Warranty and service:

The awarded vendor shall warranty and service all equipment, accessories and workmanship for no less than three calendar years after the date of project completion. The awarded vendor shall perform any warranty work or replacements free of charge to the department during this time. The awarded vendor will be responsible for scheduling and perform, at a minimum, one time per year a preventative maintenance check and tune up of their installed systems. Any defects, lubrications, parts and labor will be the vendor’s responsibility during this time frame. In the event of a system failure during the warranty period the vendor will have three business days to correct the issue and have the system running again at the vendors expense.