STATEMENT OF WORK

ANNUAL BOILER CLEANING AND INSPECTION

CLEAVER BROOKS SUMMER BOILER:  March 2018

Scope of work:

- Remove and clean burner assembly, inspect diffuse, clean and set ignition electrode.

- Drain and open waterside. Flush out any mud or sediment.

- Inspect firebox. If fire box is sooty vendor will clean fire box.

- Prep Boilers for inspector.

- Visually check all safety switches: Air pressure, low fire start switch.

- Remove and clean fuel oil strainer, if applicable.

- Close and seal waterside with new gaskets.

- Fill unit.

- Test Fire boiler and check ignition and main flame.

- Check for air leaks around door seals and other gasketed connections.

- Check for fuel leaks.

- Check low water out-off controls.

- Check operation of limit controls and modulating controls.

- Check motor amp draw and flame scanner signal.

- Perform flute gas analysis (CO, CO2 and O2) with certified calibrated flue gas analyzer.

- List any defective parts which are replaced or need to be replaced.