Specifications:

The Commonwealth of Pennsylvania Department of Corrections, of SCI Somerset located in Somerset PA requires:

Eaton MODEL 93PM-L45Kw 120/208V 4-Wire Plus Ground UPS System

Two factory-new Eaton 93PM-L60/45Kw Uninterruptible Power System for SCI Somerset.  UPS Electronics Cabinet with a self-standing Side car 4-Breaker Maintenance Bypass, PowerXpert Ethernet Communications Card and Two (2) Line-up and Matching Battery Cabinets using 390W/Cell jars to provide Ninety-Four Minutes of Back-System will enable the system to achieve over 97% efficiency during normal operation. Must provide onsite training at the request of customer’s location.

Delivery requirements - With a lead times of no more than 3 months.

This UPS will provide 125A at Full Load of 45kW.   It can be upgraded via Firmware to 60Kw, which would provide 160A (maximum current for a 200A 80% Rated Panelboard)

The 93PM 208v reaches 95% efficiency in double-conversion mode and over 97% in ESS Mode.  The double-conversion efficiency is 5% higher than your previous generation Eaton Powerware Product and is currently the highest in the industry.

No Substitute.

2) 60 Hz, Eaton 93PM-60kW Chassis UPS System, rated at:

Output Rating:               45 kV A at 1.0 pf ( 45 kV A)

UPS Input Voltage:        120/208 VAC, 3-Phase, 4-Wire plus ground

UPS Output Voltage:    120/208 VAC, 3-Phase, 4-wire plus ground,

Includes:

Eaton 93PM,60 kW Chassis-45 kV A/45 kW, 208V 4-Wire Plus Ground In/Out

•	High Efficiency (95%) Double Conversion Topology

•	Three (3) Factory Installed 20 kW Uninterruptible Power Modules (UPM)

•	The UPS is Field-Upgradeable to 50, 55, or 60 kW via Firmware

•	Advanced Battery Management Technology (ABM)

•	Ultra-Low Input Harmonic Distortion(< 3%THD)

•	Touch-Screen Display with Green/Yellow/Red LED Light Bars for System        Status.

•	Software Suite CD

•	93PM 10-60 kW UPS+ MBP Chassis Installation and Operation Manual

•	IBC-L W Cabinet Installation and Operation Manual

•	Reverse Transfer System Configuration

•	Power Xpert Gateway Card

•	Industrial Relay Interface Card

Eaton 93PM Sidecar Maint. Bypass Cabinet, 60 kW Max, 208V4-Wire + Ground In/Out

•	Line-up & Matching Cabinet, Self-Standing

•	Maintenance Bypass with 4-Breaker Design, 65 kAIC

•	Electrical Interlock with Mechanical Sliding Plate Interlock between MIS and MBP

•	Field Configurable for Single-Source or Dual Source Feed

Eaton 93PM Battery Cabinet, Large, Welded (IBC-LW) for use with a 60 kW Chassis, 480VDC

•	Line-up & Matching Cabinet with Interconnect Cables to the UPS

•	300 A DC Disconnect with 48 VDC Shunt Trip

•	One (1) String of Forty (40) 390 W/Cell VRLA Battery Jars per Cabinet

•	Back-up Runtime is 94 Minutes at 45 kW Load

Eaton 93PM Battery Cabinet Lift-Gate, Elevator Shipping Kit

•	Battery Trays Crated in Pairs, Shipped Separately from the Battery Cabinet

•	Allows use with Standard Lift-Gate, Pallet Jacks and Personnel Elevators

Services:  Warranty & Service Protection Plan, 12 Months, 7x24 Coverage, 8 Hour Response Labor to Re-Install Battery Trays in the Battery Cabinets, 5x8 Normal Business Hours Freight to Somerset, PA, FOB Destination.