SPECIFICATIONS

PA Department of Corrections

Training Academy

Elizabethtown, PA

Furnish and deliver (1) 20-75 Ton packaged industrial rooftop system with 10,000 CFM air handler to the Pennsylvania Department of Corrections Training Academy at 1451 North Market Street, Elizabethtown PA, 17022.

Equipment to be Trane InteliPak SSHLF25F or Equal

Equipment will include the following features:

- Packaged unit:

  - 25 Ton Nominal cooling capacity, R410A

  - Digital Scroll compressors

  - 230/60/3 power.

  - Low ambient operation

  - 7 day programmable Occupied/unoccupied modes of operation.

  - 36 inch Curb suitable for pad-mount installation

  - Rubber-in-shear isolators

  - Double wall construction, R13 insulated.

  - Weather resistant baked-enamel finish, meeting or exceeding ASTM B117

  - Supply air 10,000 CFM at .5” ESP, 1.99” TSP

  - Outdoor air 2,100 CFM

  - Horizontal discharge/return duct connections

  - Economizer

  - Barometric relief

  - Direct Drive Plenum Fan

  - 230/60/3 power

  - Steam heat coil per AHRI 410

  - Freeze protection (Evaporator Defrost Control)

  - AEGIS grounding bushings on motor shafts for VFD driven motors

  - Mechanical vibration cutout switch on fan

  - Stainless Steel drip pans

  - 5 year parts warranty on the fan, fan shaft, bearings, mechanical equipment supports, and fan motor

  - Supply air temp: 100ºF Heating, 60º F Cooling

- Integrated controls for Stand-alone operation with input from conventional thermostat.

- BACnet Compatible

- Minimum 11 EER combined

- FOB Jobsite